## Sheet1
1. This protocol is applicable to the integrated board MWH366 & MWH367 & MWH381. 2. The slave number can be modified by the 4x200 address, please see the address table for details. 3. The communication interface is RS485, using the standard MODUBS-RTU communication protocol, with the control board as a slave (address range: 1 to 16). 4. Data format all: 1ST + 8DATA + 1SP; Baud rate: 9600. 5. 0x, 1x, the maximum number of consecutive reads is 48, the first address of the read must be 0 or 48, otherwise incorrect data may be returned. 6. 3x, 4x, maximum number of consecutive reads is 8.
Read/Write (0x), Read: 01 / Write: 05
Register Addr. | Register Content | Range | Unit | Step | Default | Remark
0 | Power switch | 0~1 |  | 1 | 0 | 0: Switch off 1: Switch on
1 | Compulsory Defrosting | 0~1 |  | 1 | 0 | 0: Invalid 1: Enter
2 | Restore factory values (Reserved) | 0~1 |  | 1 | 0 | 0: Invalid 1: Restore factory settings
3~47 | Reserved
Read only (1x), Read: 02 / Write: --
Register Addr. | Register Content | Range | Unit | Step | Default | Remark
0 | ON/OFF | 0~1 |  |  |  | 0: OFF 1: ON (Read only)
1 | Defrosting | 0~1 |  |  |  | 0: OFF 1: ON (Read only)
2 | DIN1 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
3 | DIN2 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
4 | DIN3 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
5 | DIN4 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
6 | DIN5 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
7 | OUT1 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
8 | OUT2 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
9 | OUT3 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
10 | OUT4 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
11 | OUT5 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
12 | OUT6 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
13 | OUT7 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
14 | OUT8 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
15 | OUT9 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
16 | Malfunction / Protection indicator | 0~1 |  |  |  | 0: None 1: Yes (Read only)
17 | Compressor running demands | 0~1 |  |  |  | 0: None 1: Yes (Read only)
18 | Reserved
19 | Reserved
20 | Water Pump Status | 0~1 |  |  |  | 0: OFF 1: ON (Read only)
21~47 | Reserved
48 | E0 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
49 | E1 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
50 | E2 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
51 | E3 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
52 | E4 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
53 | E5 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
54 | E6 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
55 | E7 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
56 | E8 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
57 | E9 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
58 | EA | 0~1 |  |  |  | 0: No 1:Yes (Read only)
59 | Eb | 0~1 |  |  |  | 0: No 1:Yes (Read only)
60 | Reserved
61 | Ed | 0~1 |  |  |  | 0: No 1:Yes (Read only)
62~63 | Reserved
64 | P0 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
65 | P1 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
66 | P2 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
67 | P3 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
68 | P4 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
69 | P5 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
70 | P6 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
71 | P7 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
72 | P8 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
73 | P9 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
74 | PA | 0~1 |  |  |  | 0: No 1:Yes (Read only)
75~79 | Reserved
80 | F0 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
81 | F1 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
82 | F2 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
83 | F3 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
84 | F4 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
85 | F5 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
86 | F6 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
87 | F7 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
88 | F8 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
89 | F9 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
90 | FA | 0~1 |  |  |  | 0: No 1:Yes (Read only)
91 | Fb | 0~1 |  |  |  | 0: No 1:Yes (Read only)
92~95 | Reserved
Read/Write (4x), Read: 03 / Write: 06
Register Addr. | Register Content | Range | Unit | Step | Default | Remark
0 | Mode selection | 0~3 |  | 1 | 1 | 0: Auto 1: Heating 2: Cooling
1 | Fan speed selection | 0~2 |  | 1 | 1 | 0: Silence 1: Smart 2: Turbo (Some models without Turbo)
2 | Auto mode temperature range | 84~140 |  | 2 | 112 | Temperature type 1, see attached table for conversion formula
3 | Heating mode temperature range | 96~140 |  | 2 | 112 | Temperature type 1, see attached table for conversion formula
4 | Cooling mode temperature range | 84~120 |  | 2 | 112 | Temperature type 1, see attached table for conversion formula
5 | Water pump working mode (P0) | 0~2 |  | 1 | 0 | 0: Continuous 1: Water temp control 2: Time/water temp control
6 | Water pump working time setting (P1) | 10~120 | min | 5 | 60
7 | Compressor continuously running time between defrosting mode (P2) | 30~90 | min | 1 | 30
8 | Defrosting entry temperature (P3) | 26~60 |  | 2 | 46 | Temperature type 1, see attached table for conversion formula
9 | Maximum defrosting running time (P4) | 1~12 | min | 1 | 12
10 | Defrosting exit temperature (P5) | 76~120 |  | 2 | 86 | Temperature type 1, see attached table for conversion formula
11 | Fixed speed frequency ratio (P6) | 49~101 | % | 1 | 101 | 49 and 101 are OFF
12 | Reserved
13 | Reserved
14 | Reserved
15 | Reserved
16 | Reserved
17 | Electronic expansion valve overheat level (Heating) | 40~100 |  | 2 | 66 | Temperature type 1, see attached table for conversion formula
18 | Electronic expansion valve overheat level (Cooling) | 40~100 |  | 2 | 64 | Temperature type 1, see attached table for conversion formula
19 | Electronic expansion valve working mode | 0~1 |  | 1 | 0 | 0: Auto 1: Manual
20 | Electronic expansion valve openning setting (Heating) | 30~240 |  | 1 | 175 | Real openning = Setting value * 2
21 | Electronic expansion valve openning setting (Cooling) | 30~240 |  | 1 | 175 | Real openning = Setting value * 2
22 | Intermediate frequency ratio | 50~80 | % | 1 | 80
23 | Control way of 2nd fan motor | 0~1 |  | 1 | 0 | 0: Auto 1: Manual
24 | Fan motor speed (P19) | 10~100 | RPM | 1 | 50 | Real speed = Setting value * 9
25 | Power-off restart memory | 0~1 |  | 1 | 1 | 0: Power off 1: Restore pre-power-down state
… | Reserved
200 | Slave machine number | 1~16 |  | 1 | 1 | Example: Communications are in hexadecimal Read slave number: FF 03 00 C8 00 01 YY YY Modify slave number: FF 06 00 C8 XX XX YY YY XXXX: the slave number to be modified, YYYY: the check digit Example of modifying the slave number to 10 FF 06 00 C8 00 0A 9D ED Note: No slave number modification function for programs prior to 12 August 2022
Read only (3x), Read: 04 / Write: --
Register Addr. | Register Content | Range | Unit | Step | Default | Remark
0 | Compressor running speed percentage |  | %
1 | Compressor target frequency |  | Hz
2 | PFC voltage |  | V
3 | Water inlet temp (AIN1) |  |  |  |  | Temperature type 1, see attached table for conversion formula
4 | Water outlet temp (AIN2) |  |  |  |  | Temperature type 1, see attached table for conversion formula
5 | Ambient temp (AIN7) |  |  |  |  | Temperature type 1, see attached table for conversion formula
6 | Gas exhuast temp (AIN5) |  |  |  |  | Temperature type 2, see attached table for conversion formula
7 | Outer coil pipe temp (evaporator) (AIN3) |  |  |  |  | Temperature type 1, see attached table for conversion formula
8 | Gas return temp (AIN6) |  |  |  |  | Temperature type 1, see attached table for conversion formula
9 | Inner coil pipe temp (titanium heat exchanger) (AIN4) |  |  |  |  | Temperature type 1, see attached table for conversion formula
10 | Compressor frequency |  | Hz
11 | Compressor current |  | 0.1 A
12 | Cooling plate temp
13 | EEV openning
14 | DC fan motor speed |  | RPM
15~28 | Reserved
Appendix Contents
Temperature type 1 | Actual value = ( Displayed value - 60) / 2
Displayed value = Actual value * 2 + 60
Sample: Display value is 120, then actual temp is (120-60) / 2 = 30 ℃
Temperature type 2 | Actual value = Displayed value / 2
Displayed value = Actual value * 2
Sample: Display value is 120, then actual temp is 120 / 2 = 60 ℃