## Sheet1
1. This protocol is applicable to the PC board MWH216 & MWH298. 2. The communication interface is RS485, using MODUBS-RTU communication protocol. 3. Data format all: 1ST + 8DATA + 1SP; Baud rate: 9600. 4. In normal use, each communication of the host must be at least 60 milliseconds apart, and the slave number is 1. 5. When the host reads data: the first address must be the first address allowed in the table; the number of reads 0x,1x is fixed to 48, 3x and 4x are fixed to 3. Otherwise the slave may return incorrect data.
Tips | Read/Write (0x), Read: 01 / Write: 05
Reads allowed as first address | Register Addr. | Register Content | Range | Unit | Step | Default | Remark
| 0 | Power switch | 0~1 |  | 1 | 0 | 0: Switch off 1: Switch on
| 1 | Compulsory Defrosting | 0~1 |  | 1 | 0 | 0: Invalid 1: Enter
| 2 | Restore factory values (Reserved) | 0~1 |  | 1 | 0 | 0: Invalid 1: Restore factory settings
| 3~47 | Reserved
Tips | Read only (1x), Read: 02 / Write: --
Reads allowed as first address | Register Addr. | Register Content | Range | Unit | Step | Default | Remark
| 0 | ON/OFF | 0~1 |  |  |  | 0: OFF 1: ON (Read only)
| 1 | Defrosting | 0~1 |  |  |  | 0: OFF 1: ON (Read only)
| 2 | DIN1 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
| 3 | DIN2 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
| 4 | DIN3 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
| 5 | DIN4 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
| 6 | DIN5 | 0~1 |  |  |  | 0: Disconnected 1: Connected (Read only)
| 7 | OUT1 | 0~1 |  |  |  | 0: Closed 1: Output (Read only)
| 8 | OUT2 | 0~1 |  |  |  | 0: Closed 1: Output (Read only)
| 9 | OUT3 | 0~1 |  |  |  | 0: Closed 1: Output (Read only)
| 10 | OUT4 | 0~1 |  |  |  | 0: Closed 1: Output (Read only)
| 11 | OUT5 | 0~1 |  |  |  | 0: Closed 1: Output (Read only)
| 12 | OUT6 | 0~1 |  |  |  | 0: Closed 1: Output (Read only)
| 13 | OUT7 | 0~1 |  |  |  | 0: Closed 1: Output (Read only)
| 14 | OUT8 | 0~1 |  |  |  | 0: Closed 1: Output (Read only)
| 15 | OUT9 | 0~1 |  |  |  | 0: Closed 1: Output (Read only)
| 16 | Malfunction / Protection indicator | 0~1 |  |  |  | 0: None 1: Yes (Read only)
| 17 | Compressor running demands | 0~1 |  |  |  | 0: None 1: Yes (Read only)
| 18~47 | Reserved
Reads allowed as first address | 48 | E0 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 49 | E1 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 50 | E2 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 51 | E3 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 52 | E4 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 53 | E5 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 54 | E6 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 55 | E7 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 56 | E8 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 57 | E9 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 58 | EA | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 59 | Eb | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 60 | Reserved
| 61 | Ed | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 62~63 | Reserved
| 64 | P0 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 65 | P1 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 66 | P2 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 67 | P3 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 68 | P4 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 69 | P5 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 70 | P6 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 71 | P7 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 72 | P8 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 73 | P9 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 74 | PA | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 75~79 | Reserved
| 80 | F0 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 81 | F1 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 82 | F2 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 83 | F3 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 84 | F4 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 85 | F5 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 86 | F6 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 87 | F7 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 88 | F8 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 89 | F9 | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 90 | FA | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 91 | Fb | 0~1 |  |  |  | 0: No 1:Yes (Read only)
| 92~95 | Reserved
Tips | Read/Write (4x), Read: 03 / Write: 06
Reads allowed as first address | Register Addr. | Register Content | Range | Unit | Step | Default | Remark
| 0 | Function Selection | 0~2 |  | 1 | 1 | 0: Auto 1: Heating 2: Cooling
| 1 | Working Mode Selection | 0~3 |  | 1 | 1 | 0: Smart 1: Silence 3: Turbo (Some models without Turbo)
| 2 | Auto mode temperature range | 84~140 |  | 2 | 112 | Temperature type 1, see attached table for conversion formula
Reads allowed as first address | 3 | Heating mode temperature range | 96~140 |  | 2 | 112 | Temperature type 1, see attached table for conversion formula
| 4 | Cooling mode temperature range | 84~120 |  | 2 | 112 | Temperature type 1, see attached table for conversion formula
| 5 | Water pump working mode (P0) | 0~2 |  | 1 | 0 | 0: Continuous 1: Water temp control 2: Time/water temp control
Reads allowed as first address | 6 | Water pump working time setting (P1) | 10~120 | min | 5 | 60
| 7 | Compressor continuously running time between defrosting mode (P2) | 30~90 | min | 1 | 30
| 8 | Defrosting entry temperature (P3) | 26~60 |  | 2 | 46 | Temperature type 1, see attached table for conversion formula
Reads allowed as first address | 9 | Maximum defrosting running time (P4) | 1~12 | min | 1 | 12
| 10 | Defrosting exit temperature (P5) | 76~120 |  | 2 | 86 | Temperature type 1, see attached table for conversion formula
| 11 | Reserved
Reads allowed as first address | 12 | Reserved
| 13 | Reserved
| 14 | Reserved
Reads allowed as first address | 15 | Reserved
| 16 | Reserved
| 17 | Electronic expansion valve overheat level (Heating) | 40~100 |  | 2 | 66 | Temperature type 1, see attached table for conversion formula
Reads allowed as first address | 18 | Electronic expansion valve overheat level (Cooling) | 40~100 |  | 2 | 64 | Temperature type 1, see attached table for conversion formula
| 19 | Reserved
| 20 | Reserved
| 21 | Reserved
| 22 | Reserved
| 23 | Reserved
| 24 | Reserved
| 25 | Power-off restart memory | 0~1 |  | 1 | 1 | 0: Power off 1: Restore pre-power-down state
| 26~32 | Reserved
Tips | Read only (3x), Read: 04 / Write: --
Reads allowed as first address | Register Addr. | Register Content | Range | Unit | Step | Default | Remark
| 0 | Compressor running speed percentage |  | %
| 1 | Compressor target frequency |  | Hz
| 2 | PFC voltage |  | V
Reads allowed as first address | 3 | Water inlet temp (AIN1) |  |  |  |  | Temperature type 1, see attached table for conversion formula
| 4 | Water outlet temp (AIN2) |  |  |  |  | Temperature type 1, see attached table for conversion formula
| 5 | Ambient temp (AIN7) |  |  |  |  | Temperature type 1, see attached table for conversion formula
Reads allowed as first address | 6 | Gas exhuast temp (AIN5) |  |  |  |  | Temperature type 2, see attached table for conversion formula
| 7 | Outer coil pipe temp (evaporator) (AIN3) |  |  |  |  | Temperature type 1, see attached table for conversion formula
| 8 | Gas return temp (AIN6) |  |  |  |  | Temperature type 1, see attached table for conversion formula
Reads allowed as first address | 9 | Inner coil pipe temp (titanium heat exchanger) (AIN4) |  |  |  |  | Temperature type 1, see attached table for conversion formula
| 10 | Compressor frequency |  | Hz
| 11 | Compressor current |  | 0.1 A
Reads allowed as first address | 12 | Cooling plate temp |  |  |  |  | Temperature type 2, see attached table for conversion formula
| 13 | EEV openning
| 14 | DC fan motor speed |  | RPM
| 15~29 | Reserved
Appendix Contents
Temperature type 1 | Actual value = ( Displayed value - 60) / 2
Displayed value = Actual value * 2 + 60
Sample: Display value is 120, then actual temp is (120-60) / 2 = 30 ℃
Temperature type 2 | Actual value = Displayed value / 2
Displayed value = Actual value * 2
Sample: Display value is 120, then actual temp is 120 / 2 = 60 ℃